## Load Calculation
Heat Loss Calculation Table
Deg F
Indoor Dsg Temp
Outdoor Dsg Temp
Earth Temp
Contractor | [6 empty] | Job Name/Address | [6 empty] | Date:
1 | Space under consideration | [5 empty] | Crawlspace |  | Basement |  | Main Floor |  | Upper Floor |  | Entire Building
2 | Running perimeter of exterior wall (feet) | [13 empty] | 0
3 | Floor area (square feet) | [13 empty] | 0
4 | Wall height (feet) | [13 empty] | 0
TYPE OF EXPOSURE |  | Material |  | R | U | ΔT | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr | Area | BTU/hr
5 | Net exposed walls | A. | Concrete earth | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  | B. | Concrete air | 10 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | C. | Primary wall mat'l to air | 18 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | D. | Alt. Wall mat'l to air | 19 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
6 | Windows and Glass doors | E. | Window | 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | G. | Glass door |  | 0.5 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
7 | Solid doors | H. |  | 8 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
8 | Gross ceiling | I. | Flat ceiling | 38 |  | 0 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
| Skylights | J. |  |  | 0.5 | 0 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
8a | Gross ceiling | Ia. | Sloped ceiling | 38 |  | 0 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
Ceiling Pitch on 12
| Skylights | Ja. |  |  | 0.5 | 0 |  |  |  | 0 |  | 0 |  | 0 | 0 | 0
9 | Floors on earth | K. | Include insulation | 10 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
10 | Floors over unheated | L. |  | 19 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
12 | Building Envelope Heat Loss | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0
13 | Infiltration Heat Loss- Air Change/Hr |  |  | ACH |  | 0.5 | 0 |  | 0 |  | 0 |  | 0 |  | 0
14 | Total Heat Loss | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0
16 | Efficiency deration | Efficiency of heating equipment |  |  |  |  | Input |  | Input |  | Input |  | Input |  | Total Input
[5 empty] | 100% |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
form release: 12/09/2003
revised 05/20/09 JRS
Directions:
1 | Enter or modify information in the |  |  | blue | cells only. All other cells are locked.
2 | See R-value work sheet for values. DO NOT enter both R and U values. This worksheet defaults to the R value. If you want to use the U value, leave the R value empty.
3 | The values listed in the R and U columns are the most common but should be modified to correspond to building materials actually used.
4 | Enter the area values in square feet.
5 | The Yellow area cells are locked and calculate the residual area. If these values are negitive, you will get an error message.
6 | For further direction, cells with a red triangle offer additional comments when the cursor is placed over the cell.
7 | When finished, print this form and attach it to your plans for review.
Note on B11: Enter the average wall height for each story measured from floor surface of one floor to the floor surface of the floor above.
Note on H11: For crawlspaces, enter the height from grade to the top of the floor above.
Note on D13: The foundation wall surface area that is in contact with soil. Calculated for you.
Note on H13: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on J13: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on D14: Enter the foundation wall surface area in contact with outside air.
Note on L15: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on N15: These cells are locked in order to verify proper sum of areas. If you get a negative number, your areas do not match the perimeter times wall height.
Note on B19: Include any doors than have less than 50% glazing.
Note on B20: Assumes insulation at the ceiling joist or bottom chord of trusses. Enter the flat area of the entire ceiling, including any skylights.
Note on I20: A crawlspace does not have a roof, it has a floor over it. Enter any floor insulation values in floor of the level above.
Note on B22: Assumes rafter or scissor truss construction. Enter the flat area of the entire roof, including any skylights. Pitch is taken into account in the next row.
Note on B23: Enter the pitch of the INTERIOR surface of a cathedral or vaulted ceiling. This is the vertical RISE for a horizontal RUN of 12.
Note on B25: Enter the foor area incontact with the earth
Note on B26: These include: Garages, crawlspaces and similar construction where the floor is over unheated but enclosed construction.
Note on P27: This is the summary that should appear on the Heat Loss Certificate.
Note on F31: This information is usually listed on the appliance, or available from the supplier. This value cannot be lower than 80%.
Note on P31: This is the minimum heat input required to meet the heat loss as calculated.
Note on D15: Primariy Wall calculated for you

## R-Values
Calculating Assembly Wall R-Value*
Formula: Assembly R-value = 1 / (Assembly U-value) = 1 / (U-studs x % + U-cavity x %)
Component | R-Value Studs | R-Value Cavity | Assembly R-Value
Wall - Outside Air Film | 0.17 | 0.17
Siding - Wood Bevel | 0.8 | 0.8
Plywood Sheathing - 1/2" | 0.63 | 0.63
5 1/2" Fiberglass Batt |  | 17
5 1/2" Stud | 6.88
1/2" Drywall | 0.45 | 0.45
Inside Air Film | 0.68 | 0.68
Percent for 16" o.c. + Additional studs | 15% | 85%
Total Wall Component R-Values | 9.61 | 19.73
Wall Component U-Values | 0.10406 | 0.050684
Total Wall Assembly R-Value |  |  | 18.212
* This example is just for wood frame construction. Steel studs are a more complicated calculation.
R-Value Table
Material | R/ | R/
| Inch | Thickness
Insulation Materials
Fiberglass Batt | 3.14-4.30
Fiberglass Blown (attic) | 2.20-4.30
Fiberglass Blown (wall) | 3.70-4.30
Rock Wool Batt | 3.14-4.00
Rock Wool Blown (attic) | 3.10-4.00
Rock Wool Blown (wall) | 3.10-4.00
Cellulose Blown (attic) | 3.13
Cellulose Blown (wall) | 3.7
Vermiculite | 2.13
Autoclaved Aerated Concrete | 1.05
Urea Terpolymer Foam | 4.48
Rigid Fiberglass (> 4lb/ft3) | 4
Expanded Polystyrene (beadboard) | 4
Extruded Polystyrene | 5
Polyurethane (foamed-in-place) | 6.25
Polyisocyanurate (foil-faced) | 7.2
Construction Materials
Concrete Block 4" |  | 0.8
Concrete Block 8" |  | 1.11
Concrete Block 12" |  | 1.28
Brick 4" common |  | 0.8
Brick 4" face |  | 0.44
Poured Concrete | 0.08
Soft Wood Lumber | 1.25
2" nominal (1 1/2") |  | 1.88
2x4 (3 1/2") |  | 4.38
2x6 (5 1/2") |  | 6.88
Cedar Logs and Lumber | 1.33
Sheathing Materials
Plywood | 1.25
1/4" |  | 0.31
3/8" |  | 0.47
1/2" |  | 0.63
5/8" |  | 0.77
3/4" |  | 0.94
Fiberboard | 2.64
1/2" |  | 1.32
25/32" |  | 2.06
Fiberglass (3/4") |  | 3
(1") |  | 4
(1 1/2") |  | 6
Extruded Polystyrene (3/4") |  | 3.75
(1") |  | 5
(1 1/2") |  | 7.5
Foil-faced Polyisocyanurate |  | 5.4
(3/4")
(1") |  | 7.2
(1 1/2") |  | 10.8
Siding Materials
Hardboard (1/2") |  | 0.34
Plywood (5/8") |  | 0.77
(3/4") |  | 0.93
Wood Bevel Lapped |  | 0.8
Aluminum, Steel, Vinyl |  | 0.61
(hollow backed)
(w/ 1/2" Insulating board) |  | 1.8
Brick 4" |  | 0.44
Interior Finish Materials
Gypsum Board (drywall 1/2") |  | 0.45
(5/8") |  | 0.56
Paneling (3/8") |  | 0.47
Flooring Materials
Plywood | 1.25
(3/4") |  | 0.93
Particle Board (underlayment) | 1.31
(5/8") |  | 0.82
Hardwood Flooring | 0.91
(3/4") |  | 0.68
Tile, Linoleum |  | 0.05
Carpet (fibrous pad) |  | 2.08
(rubber pad) |  | 1.23
Roofing Materials
Asphalt Shingles |  | 0.44
Wood Shingles |  | 0.97
Windows
Single Glass |  | 0.91
w/storm |  | 2
Double insulating glass |  | 1.61
(3/16") air space
(1/4" air space) |  | 1.69
(1/2" air space) |  | 2.04
(3/4" air space) |  | 2.38
(1/2" w/ Low-E 0.20) |  | 3.13
(w/ suspended film) |  | 2.77
(w/ 2 suspended films) |  | 3.85
(w/ suspended film and low-E) |  | 4.05
Triple insulating glass |  | 2.56
(1/4" air spaces)
(1/2" air spaces) |  | 3.23
Addition for tight fitting drapes or shades, or closed blinds |  | 0.29
Doors
Wood Hollow Core Flush |  | 2.17
(1 3/4")
Solid Core Flush (1 3/4") |  | 3.03
Solid Core Flush (2 1/4") |  | 3.7
Panel Door w/ 7/16" Panels |  | 1.85
(1 3/4")
Storm Door (wood 50% glass) |  | 1.25
(metal) |  | 1
Metal Insulating |  | 15
(2" w/ urethane)
Air Films
Interior Ceiling |  | 0.61
Interior Wall |  | 0.68
Exterior |  | 0.17
Air Spaces
1/2" to 4" approximately |  | 1

## Design Temperatures
D
State | City | January |  |  |  | July
|  | Dry Bulb Temperature (oF) | Normal Relative Humidity (%) |  |  | Dry Bulb Temperature (oF) | Normal Relative Humidity (%)
|  |  | 7:30 | 13:30 | 19:30 |  | 7:30 | 13:30 | 19:30
Alabama | Birmingham | 10 | 81 | 61 | 66 | 95 | 84 | 56 | 68
| Mobile | 10 |  |  |  | 95 | 90 | 64 | 78
Arizona | Flagstaff | -10 | 83 | 58 |  | 90 | 77 | 36
| Phoenix | 25 | 75 | 47 | 39 | 100 | 53 | 31 | 23
| Yuma | 30 | 56 | 37 | 27 | 105 | 51 | 31 | 23
Arkansas | Little Rock | 5 | 80 | 67 | 68 | 110 | 85 | 55 | 59
California | Eureka | 30 | 87 |  | 77 | 95 | 92 |  | 80
| Fresno | 25 | 93 | 80 | 66 | 90 | 61 | 36 | 20
| Los Angeles | 35 | 63 | 46 | 51 | 105 | 85 | 50 | 54
| Sacramento | 30 | 90 | 82 | 70 | 90 | 76 | 46 | 28
| San Diego | 35 | 76 | 58 | 60 | 100 | 86 | 68 | 65
| San Francisco | 35 | 84 | 69 | 70 | 85 | 92 | 75 | 78
Colorado | Denver | -10 | 54 | 37 | 41 | 85 | 55 | 27 | 30
| Grand Junction | -15 | 77 | 64 | 64 | 95 | 48 | 27 | 22
| Pueblo | -20 | 67 | 44 | 48 | 95 | 73 | 34 | 35
Connecticut | New Haven | 0 | 75 | 65 | 69 | 95 | 77 | 64 | 74
Delaware | Wilmington | 0 | 77 | 62 | 70 | 95 | 80 | 52 | 69
District of Columbia | Washington | 0 | 73 | 56 | 64 | 95 | 78 | 52 | 64
Florida | Jacksonville | 25 | 89 | 56 | 75 | 95 | 85 | 57 | 76
| Miami | 35 | 87 | 59 | 75 | 91 | 83 | 64 | 76
Georgia | Atlanta | 10 | 80 | 64 | 69 | 95 | 83 | 57 | 68
| Augusta | 10 | 84 | 59 | 69 | 98 | 83 | 55 | 69
| Savannah | 20 | 83 | 58 | 72 | 95 | 85 | 61 | 80
Idaho | Boise | -10 | 82 | 75 | 74 | 95 | 54 | 34 | 23
| Lewiston | -5 | 79 | 73 | 71 | 95 | 64 | 37 | 25
Illinois | Cairo | 0 | 81 | 69 |  | 98 | 83 | 57
| Chicago | -10 | 81 | 70 | 75 | 95 | 78 | 51 | 55
| Peoria | -10 | 73 | 72 | 77 | 96 | 81 | 53 | 58
Indiana | Fort Wayne | -10 | 84 | 75 | 81 | 95 | 84 | 53 | 58
| Indianapolis | -10 | 83 | 72 | 78 | 95 | 84 | 54 | 60
| Terre Haute | 0 | 82 | 70 | 76 | 95 | 77 | 50 | 56
Iowa | Davenport | -15 |  |  |  | 95
| Sioux City | -20 | 78 | 67 | 72 | 95 | 86 | 55 | 54
Kansas | Dodge City | -10 | 78 | 57 | 61 | 95 | 77 | 45 | 52
| Topeka | -10 | 78 | 64 | 67 | 100 | 85 | 54 | 54
Kentucky | Louisville | 0 | 78 | 68 | 69 | 95 | 77 | 52 | 57
Louisiana | New Orleans | 20 | 85 | 67 | 73 | 95 | 84 | 64 | 72
| Shreveport | 20 | 83 | 67 | 66 | 100 | 86 | 56 | 62
Maine | Portland | -5 | 81 | 65 | 74 | 90 | 78 | 58 | 76
Maryland | Baltimore | 0 | 72 | 68 | 56 | 95 | 71 | 52 | 65
Massachusetts | Boston | 0 | 72 | 59 | 67 | 92 | 72 | 55 | 70
Michigan | Detroit | -10 | 82 | 71 | 77 | 95 | 74 | 50 | 56
| Grand Rapids | -10 | 85 | 78 | 80 | 95 | 76 | 51 | 54
Minnesota | Duluth | -25 | 78 | 74 | 74 | 93 | 87 | 61 | 66
| Minneapolis | -20 | 82 | 72 | 75 | 95 | 82 | 54 | 54
Mississippi | Vicksburg | 10 | 82 | 65 | 67 | 95 | 87 | 61 | 70
Missouri | Kansas City | -10 | 78 | 64 | 66 | 100 | 76 | 48 | 47
| St. Louis | 0 | 77 | 65 | 68 | 95 | 73 | 50 | 55
Montana | Billings | -25 | 67 | 73 | 60 | 90 | 65 | 40 | 33
| Butte | -20 | 76 | 70 | 71 | 95 | 82 | 36 | 33
Nebraska | North Platte | -20 | 80 | 62 | 66 | 85 | 84 | 50 | 46
| Omaha | -10 | 82 | 68 | 73 | 65 | 780 | 51 | 51
Nevada | Reno | -5 | 82 | 67 | 54 | 95 | 72 | 25 | 20
New Hampshire | Concord | -15 | 78 | 60 | 69 | 90 | 80 | 49 | 69
New Jersey | Atlantic City | 5 | 79 | 68 | 74 | 95 | 81 | 72 | 82
| Newark | 0 | 72 | 79 | 65 | 95 | 75 | 51 | 65
| Trenton | 0 | 73 | 62 | 68 | 95 | 77 | 55 | 68
New Mexico | Albuquerque | 0 | 68 | 51 | 46 | 95 | 59 | 33 | 28
New York | Albany | -10 | 75 | 63 | 71 | 93 | 79 | 52 | 64
| Buffalo | -5 | 79 | 72 | 78 | 93 | 78 | 53 | 63
| New York | 0 | 72 | 61 | 66 | 95 | 75 | 58 | 68
| Rochester | -5 | 81 | 73 | 79 | 95 | 80 | 50 | 60
North Carolina | Asheville | 0 | 82 | 59 | 69 | 93 | 88 | 56 | 73
| Raleigh | 10 | 82 | 57 | 69 | 95 | 86 | 55 | 72
North Dakota | Bismarck | -30 | 77 | 71 | 75 | 95 | 85 | 52 | 49
Ohio | Cincinnati | 0 | 82 | 70 | 74 | 95 | 84 | 52 | 60
| Cleveland | 0 | 81 | 72 | 79 | 95 | 79 | 52 | 58
| Columbus | -10 | 83 | 71 | 76 | 95 | 78 | 52 | 60
| Toledo | -10 | 79 | 72 | 75 | 95 | 76 | 52 | 59
Oklahoma | Oklahoma City | 0 | 79 | 62 | 65 | 101 | 80 | 49 | 51
Oregon | Baker | -5 | 83 | 81 | 78 | 90 | 69 | 68 | 36
| Portland | 10 | 87 | 82 | 78 | 90 | 86 | 63 | 48
Pennsylvania | Harrisburg | 0 | 72 | 49 | 65 | 95 | 78 | 51 | 62
| Philadelphia | 0 | 74 | 65 | 68 | 95 | 78 | 52 | 65
| Pittsburgh | 0 | 77 | 67 | 63 | 95 | 80 | 52 | 63
| Scranton | -5 | 80 | 67 |  | 95 | 77 | 50
Rhode Island | Providence | 0 | 73 | 60 | 67 | 93 | 79 | 57 | 73
South Carolina | Charleston | 15 | 87 | 55 | 76 | 95 | 88 | 64 | 82
| Columbia | 10 | 81 | 57 | 65 | 95 | 83 | 56 | 68
South Dakota | Huron | -20 | 79 | 72 | 76 | 95 | 86 | 52 | 49
| Rapid City | -20 | 71 | 69 | 67 | 95 | 71 | 42 | 40
Tennessee | Knoxville | 0 | 83 | 65 | 69 | 95 | 83 | 55 | 66
| Memphis | 0 | 82 | 67 | 73 | 95 | 85 | 55 | 59
Texas | Amarillo | -10 | 71 | 51 | 52 | 100 | 77 | 43 | 42
| Corpus Christi | 20 | 88 | 66 | 75 | 95 | 93 | 58 | 68
| Dallas | 10 | 81 | 62 | 62 | 100 | 79 | 50 | 47
| El Paso | 10 | 63 | 45 | 39 | 100 | 60 | 37 | 30
| Houston | 20 | 85 | 66 | 73 | 95 | 90 | 58 | 66
| San Antonio | 20 | 82 | 60 | 59 | 100 | 88 | 49 | 45
Utah | Salt Lake City | -10 | 80 | 71 | 72 | 95 | 56 | 27 | 23
Vermont | Burlington | -10 | 81 | 69 | 78 | 90 | 76 | 54 | 67
Virginia | Richmond | 15 | 84 | 60 | 68 | 95 | 81 | 57 | 72
Washington | Seattle | 15 | 86 | 80 | 74 | 85 | 86 | 63 | 47
| Walla Walla | -5 | 80 | 74 | 78 | 95 | 50 | 33 | 22
West Virginia | Charleston | 0 | 79 | 64 | 70 | 95 | 88 | 53 | 67
| Parkersburg | -10 | 82 | 66 | 74 | 95 | 80 | 52 | 65
Wisconsin | Green Bay | -15 | 75 | 68 | 73 | 95 | 85 | 58 | 64
| Milwaukee | -15 | 76 | 70 | 73 | 95 | 81 | 58 | 64
Wyoming | Cheyenne | -15 | 59 | 48 | 55 | 95 | 73